## Heating Sizing
Simple Heating System Size: Washington State
This heating system sizing calculator is based on the Prescriptive Requirements of the 2018 Washington State Energy Code (WSEC) and ACCA Manuals J and S. This tool will calculate heating loads only. ACCA procedures for sizing cooling systems should be used to determine cooling loads. Please complete the green drop-downs and boxes that are applicable to your project. As you make selections in the drop-downs for each section, some values will be calculated for you. If you do not see the selection you need in the drop-down options, please contact the WSU Energy Program at energycode@energy.wsu.edu or (360) 956-2042 for assistance.
| Project Information | [5 empty] | Contact Information
Heating System Type:
To see detailed instructions for each section, place your cursor on the word "Instructions"
Design Temperature
|  |  |  | Instructions |  |  | Design Temperature Difference (∆T) |  |  |  |  | 68
∆T = Indoor (70 degrees) - Outdoor Design Temp
Area of Building
Conditioned Floor Area
|  |  |  | Instructions | Conditioned Floor Area (sq ft)
|  |  | Average Ceiling Height | [5 empty] | Conditioned Volume
|  |  |  | Instructions | Average Ceiling Height (ft) |  |  |  | ________
|  | Glazing and Doors |  |  |  |  | U-Factor | X | Area | = | UA
|  |  |  | Instructions |  |  | No selection |  |  |  | ---
|  | Skylights |  |  |  |  | U-Factor | X | Area | = | UA
|  |  |  | Instructions |  |  | 0.5 |  |  |  | ---
Insulation
|  |  | Attic |  |  |  | U-Factor | X | Area | = | UA
|  |  |  | Instructions |  |  | No selection |  |  |  | ---
|  |  | Single Rafter or Joist Vaulted Ceilings |  |  |  | U-Factor | X | Area |  | UA
|  |  |  | Instructions |  |  | No selection |  |  |  | ---
|  |  | Above Grade Walls (see Figure 1) |  |  |  | U-Factor | X | Area |  | UA
|  |  |  | Instructions |  |  | No selection |  |  |  | ---
|  |  | Floors |  |  |  | U-Factor | X | Area |  | UA
|  |  |  | Instructions |  |  | No selection |  |  |  | ---
|  |  | Below Grade Walls (see Figure 1) |  |  |  | U-Factor | X | Area |  | UA
|  |  |  | Instructions |  |  | No selection |  |  |  | ---
|  |  | Slab Below Grade (see Figure 1) |  |  |  | F-Factor | X | Length |  | UA
|  |  |  | Instructions |  |  | No selection |  |  |  | ---
|  |  | Slab on Grade (see Figure 1) |  |  |  | F-Factor | X | Length |  | UA
|  |  |  | Instructions |  |  | No selection |  |  |  | ---
Location of Ducts
|  |  |  | Instructions |  |  |  |  | Duct Leakage Coefficient
1.1
[6 empty] | Sum of UA |  |  |  |  | _________
[6 empty] | Envelope Heat Load |  |  |  |  | _________ | Btu / Hour
Sum of UA x ∆T
[6 empty] | Air Leakage Heat Load |  |  |  |  | _________ | Btu / Hour
Volume x 0.6 x ∆T x 0.018
[6 empty] | Building Design Heat Load |  |  |  |  | _________ | Btu / Hour
Air leakage + envelope heat loss
[6 empty] | Building and Duct Heat Load |  |  |  |  | _________ | Btu / Hour
Ducts in unconditioned space: sum of building heat loss x 1.10
Ducts in conditioned space: sum of building heat loss x 1
[6 empty] | Maximum Heat Equipment Output |  |  |  |  | _________ | Btu / Hour
Building and duct heat loss x 1.40 for forced air furnace
Building and duct heat loss x 1.25 for heat pump
Above Grade
Below Grade
Figure 1.
All Other Systems
Heat Pump
Note on G12: Using the drop-down, select the city that is closest to your building site.
Note on G17: Using exterior measurements, enter the square footage of living space conditioned directly or indirectly.
Note on G20: Enter the average ceiling height from your building plans.
Note on G23: Calculate and enter the total area of the vertical fenestration products (windows and doors) in the structure. Example: Window #1 area 10 ft2 Window #2 area 15 ft2 Total area 25 ft2 The glazing and doors portion of this calculator assumes the installed glazing products have an area weighted average U-factor
Note on G25: Calculate and enter the total area of the skylights in the structure. Example: Skylight #1 area 10 ft2 Skylight #2 area 15 ft2 Total area 25 ft2 The skylight portion of this calculator assumes the installed skylight products have an area weighted average U-factor of 0.30.
Note on G29: Using the drop-down, select the R-value specified in your building plans for flat and/or scissor truss ceilings. Then calculate and enter the area of the ceiling under attic insulated with the selected R-value.
Note on G32: Using the drop-down, select the R-value specified in your building plans for vaulted ceilings. Then calculate and enter the area of the vaulted ceiling insulated with the selected R-value. If there are no vaulted ceilings, select "No Vaulted Ceilings in this project"
Note on G35: Using the drop-down, select the R-value specified in your building plans for the above grade walls. Then calculate and enter the net above grade wall area. Net above grade wall area is the total above grade wall area minus the area of windows and doors. See Figure 1 for help understanding above and below grade.
Note on G38: Using the drop-down, select the R-value specified in your building plans for floors above conditioned and/or unconditioned spaces. Then calculate and enter the floor area with the selected R-value.
Note on G41: Using the drop-down, select the R-value specified in your building plans for the below grade walls. Then calculate and enter the net below grade wall area. Net below grade wall area is the total below grade wall area minus the area of windows and doors.
Note on G44: Using the drop-down, select the insulation status specified in your building plans for the Below Grade Walls. Then calculate and enter the linear feet of perimeter of the slab below grade. For example, if the basement floor is a 54' x 32' slab below grade, the linear perimeter would be 172ft . 54'+54'+32'+32' = 172'
Note on G47: Using the drop-down, select the R-value specified in your building plans for slab on grade. Then calculate and enter the linear feet of perimeter of the slab on grade. For example, if the living room is a 20' x 30' slab on grade, the linear perimeter would be 100 ft. 20'+20'+30'+30'=100'
Note on G51: Using the drop-down, indicate if the majority of ducts will be installed in conditioned or unconditioned spaces. - If the majority of ducts will be installed in living areas, or if the heating system will be ductless, select "Conditioned Space" - If the majority of ducts will be installed in unconditioned space (crawlspace or unconditioned basement), select "Unconditioned Space"

## LookUps (hidden)
Each of these sections contain on row 2 the result of the selections, and three columns: a lookup number for formulas, selections for drop down boxes, and the measurement to use in the formulas.
|  | 36 |  |  | 1 |  |  | 1 |  |  | 1 |  |  | 1 |  |  | 1 |  |  | 1 |  |  | 1 |  |  | 1 |  |  | 3 |  |  | 2
Indoor Design Temperature |  | Outdoor Design Temperature |  |  | Vertical Glazing and Doors |  |  | Attic |  |  | Single Rafter or Joist Vaulted Ceilings |  |  | Above Grade Walls |  |  | Floors |  |  | Below Grade Walls |  |  | Slab Below Grade |  |  | Slab on Grade |  |  | Location of Ducts |  | Heating System Type
70 | Column1 | City | Temp | Column1 | R-Value | U-Factor | Column1 | R-Value | U-Factor | Column1 | R-Value | U-Factor | Column1 | R-Value | U-Factor | Column1 | R-Value | U-Factor | Column1 | R-Value | U-Factor | Column1 | R-Value | F-Factor | Column1 | R-Value | F-Factor | Offset | location of ducts | Heat loss correction
| 1 | Select closest city |  | 1 | Select U-Factor | No selection | 1 | Select R-Value | No selection | 1 | Select R-Value | No selection | 1 | Select R-Value | No selection | 1 | Select R-Value | No selection | 1 | Select R-value | No selection | 1 | Select conditioning | No selection | 1 | Select R-Value | No selection | 1 | Select Location of Ducts |  | Forced Air Furnace | 1 | 1.4
| 2 | Aberdeen 20 NNE | 25 | 2 | U-0.30 | 0.3 | 2 | R-49 | 0.026 | 2 | R-38 Vented | 0.027 | 2 | R-21 Intermediate | 0.056 | 2 | R-30 | 0.029 | 2 | R-21 Interior | 0.042 | 2 | R-5 Thermal Break at slab edge | 0.57 | 2 | R-10 Perimeter | 0.54 | 2 | Conditioned Space | 1 | Heat Pump | 2 | 1.25
| 3 | Anacortes | 24 | 3 | U-0.28 | 0.28 | 3 | R-38 Advanced | 0.026 | 3 | R-49 Advanced | 0.02 | 3 | R-21 INT plus R-4 ci | 0.043 | 3 | R-38 | 0.025 | 3 | R-10 Continuous Exterior | 0.064 | 3 | R-10 Fully insulated | 0.303 | 3 | R-10 Fully Insulated | 0.36 | 3 | Unconditioned Space | 1.1
| 4 | Anatone | -4 | 4 | U-0.25 | 0.25 |  |  |  | 4 | No Vaulted Ceilings in this project. | --- | 4 | R-21 INT plus R-12 ci | 0.032 | 4 | No Floors above unconditioned spaces. | --- | 4 | R-21 int plus R-5 ci | 0.028 | 4 | No Slab Below Grade in this project. |  | 4 | No Slab on Grade in this project. | --- | 4 | No Ducts | 1
| 5 | Appleton | 11 | 5 | U-0.24 | 0.24 | [12 empty] | 5 | R-21 int plus R-12 ci | 0.021 | 5 | R-21 int Plus R-5 ci | 0.56
| 6 | Auburn | 25 | 6 | U-0.22 | 0.22 | [12 empty] | 6 | No Below Grade Walls in this project. | --- | 6 | R-21 int Plus R-12 ci | 0.57
| 7 | Battleground | 19 | [16 empty] | From original form
| 8 | Bellevue | 24 | [16 empty] | 2' Depth Walls | 0.042 |  | From original form
| 9 | Bellingham 2N | 19 | [16 empty] | 3.5' Depth Walls | 0.041 |  | 2' Depth | 0.59
| 10 | Benton City 2 NW | 11 | [16 empty] | 7' Depth Walls | 0.037 |  | 3.5' Depth | 0.64
| 11 | Bickleton | 4 | [16 empty] | Other |  |  | 7' Depth | 0.57
| 12 | Blaine | 17 | [19 empty] | Other
| 13 | Bothell 2 N | 17
| 14 | Bremerton | 29
| 15 | Brier | 24
| 16 | Buckley 1 NE | 26
| 17 | Bumping Lake | -5
| 18 | Burlington | 19
| 19 | Camas | 21
| 20 | Castle Rock | 23
| 21 | Cedar Lake | 20
| 22 | Centralia | 21
| 23 | Central Park | 27
| 24 | Chehalis | 21
| 25 | Chelan | 10
| 26 | Cheney | 4
| 27 | Chesaw | -11
| 28 | Chewalah 2 S | -9
| 29 | Chief Joseph Dam | 6
| 30 | Clallam Bay 1 NNE | 28
| 31 | Clarkston | 10
| 32 | Clearbrook | 19
| 33 | Clearwater | 26
| 34 | Cle Elum | 1
| 35 | Clyde Hill | 24
| 36 | Colfax 1 NW | 2
| 37 | College Place | 6
| 38 | Colville AP | -2
| 39 | Conconully | -7
| 40 | Concrete | 19
| 41 | Connell 4 NNW | 6
| 42 | Cougar 5 E | 25
| 43 | Coulee Dam 1 SW | 9
| 44 | Coupeville 1 S | 21
| 45 | Cushman Dam | 22
| 46 | Dallesport AP | 14
| 47 | Darrington RS | 13
| 48 | Davenport | 5
| 49 | Dayton 1 WSW | 5
| 50 | Deer Park 2 E | -5
| 51 | Des Moines | 25
| 52 | Diablo Dam | 15
| 53 | Dishman | 9
| 54 | East Bremerton | 29
| 55 | Edmonds | 24
| 56 | Electron Headwks | 16
| 57 | Ellensburg AP | 2
| 58 | Elma | 24
| 59 | Eltopia 6 W | 9
| 60 | Elwha RS | 24
| 61 | Enumclaw | 26
| 62 | Ephrata AP | 7
| 63 | Everett JC | 23
| 64 | Everett Paine AFB | 21
| 65 | Fircrest | 29
| 66 | Forks I E | 23
| 67 | Fort Lewis | 24
| 68 | Fruitvale | 1.1
| 69 | Glacier RS | 13
| 70 | Glenoma (Kosmos) | 18
| 71 | Goldendale | 7
| 72 | Grandview | 12
| 73 | Grapeview | 30
| 74 | Grayland 2 S | 28
| 75 | Grays River Hatchery | 24
| 76 | Greenwater | 1.4
| 77 | Grotto | 21
| 78 | Harrington 2 S | 3
| 79 | Hartline | 7
| 80 | Hatton 8 E | 1
| 81 | Holden Village | 4
| 82 | Hoquiam AP | 26
| 83 | Ice Harbor Dam | 17
| 84 | Inchelium 2 NW | 0
| 85 | Issaquah | 23
| 86 | John Day Dam | 19
| 87 | Kelso AP | 24
| 88 | Kennewick 10 SW | 13
| 89 | Kent | 21
| 90 | Kid Valley | 20
| 91 | Kirkland | 17
| 92 | Lacey | 17
| 93 | Lacrosse 3 ESE | -3
| 94 | La Grande | 23
| 95 | Lake Cle Elum | -4
| 96 | Lake Forest Park | 20
| 97 | Lake Kachess | -2
| 98 | Lake Keechelus | 0
| 99 | Lakewood Center | 23
| 100 | Landsburg | 18
| 101 | Larson AFB | 6
| 102 | Laurier | -8
| 103 | Leavenworth | -3
| 104 | Lemanasky Lake | -7
| 105 | Lind 3 NE | 6
| 106 | Linwood | 10
| 107 | Little Goose Dam | 22
| 108 | Long Beach 3 NNE | 25
| 109 | Longview | 24
| 110 | Lower Granite Dam | 14
| 111 | Lower Monument Dam | 18
| 112 | Lynden | 18
| 113 | Lynnwood | 24
| 114 | Maloft | 4
| 115 | Marietta 3 NNW | 18
| 116 | Marysville | 23
| 117 | McMillin Res. | 21
| 118 | McNary Dam | 11
| 119 | Medical Lake | 4
| 120 | Medina | 24
| 121 | Mercer Island | 25
| 122 | Metaline Falls | -1
| 123 | Methow 2 W | 1
| 124 | Mountlake Terrace | 22
| 125 | Mt. Spokane Summit | -2
| 126 | Mount Vernon 3 WNW | 20
| 127 | Moxee City 10 E | 8
| 128 | Mud Mtn. Dam | 23
| 129 | Nespelem 2 S | -4
| 130 | Newhalem | 19
| 131 | Newport | -5
| 132 | Normandy Park | 24
| 133 | Northport | 2
| 134 | Oak Harbor | 16
| 135 | Oakville | 20
| 136 | Odessa | 7
| 137 | Olga 2 SE | 24
| 138 | Olympia, AP. | 17
| 139 | Omak 2 NW | 3
| 140 | Opportunity | 8
| 141 | Oroville | 5
| 142 | Othello | 9
| 143 | Packwood | 16
| 144 | Palmer 3 SE | 22
| 145 | Parkland | 20
| 146 | Pasco | 13
| 147 | Plain | -3
| 148 | Pleasant View | 16
| 149 | Pt. Grenville | 27
| 150 | Pomeroy | 3
| 151 | Port Angeles | 28
| 152 | Port Orchard | 29
| 153 | Port Townsend | 25
| 154 | Priest Rapids Dam | 14
| 155 | Prosser | 12
| 156 | Pullman Exp. Sta. | 1
| 157 | Puyallup | 19
| 158 | Quilcene 2 SW | 23
| 159 | Quillayute AP | 23
| 160 | Quinault RS | 25
| 161 | Quincy 1 NE | 4
| 162 | Rainier, Longmire | 15
| 163 | Paradise RS | 8
| 164 | Raymond | 28
| 165 | Redmond | 17
| 166 | Renton | 24
| 167 | Republic | -9
| 168 | Richland | 11
| 169 | Rimrock Tieton Dam | 4
| 170 | Ritzville | 6
| 171 | Rosalia | 6
| 172 | Ross Dam | 14
| 173 | St. John | 15
| 174 | Sappho 8 E | 23
| 175 | Satus Pass | 10
| 176 | Seattle: Sea-Tac AP | 24
| 177 | Sedro Woolley 1 E | 19
| 178 | Selah | 11
| 179 | Sequim | 23
| 180 | Shelton | 23
| 181 | Shoultes | 23
| 182 | Skamania Fish Hatch. | 24
| 183 | Smyrna | 8
| 184 | Snohomish | 21
| 185 | Snoqualmie Falls | 22
| 186 | Snoqualmie Pass | 6
| 187 | South Broadway | 11
| 188 | So. Olympic Tree Farm | 24
| 189 | Spanaway | 20
| 190 | Spokane AP | 4
| 191 | Spokane CO | 10
| 192 | Spokane Fairchild AFB | 4
| 193 | Sprague | 4
| 194 | Stampede Pass | 7
| 195 | Startup 1 E | 20
| 196 | Stehekin 3 NW | 12
| 197 | Steilacoom | 21
| 198 | Stevens Pass | 6
| 199 | Stockdill Ranch | -14
| 200 | Sumner | 19
| 201 | Sunnyside | 12
| 202 | Tacoma McChord | 21
| 203 | Tacoma CO | 29
| 204 | Tatoosh Island | 31
| 205 | Thompson Place | 20
| 206 | Tietort Intake | 6
| 207 | Toledo AP | 17
| 208 | Toppenish | 11
| 209 | Trinidad 2 SSE | 13
| 210 | Tukwila | 24
| 211 | Tumwater | 17
| 212 | University Place | 29
| 213 | Upper Baker Dam | 14
| 214 | Vancouver | 22
| 215 | Vashon Island | 28
| 216 | Walla Walla AP | 6
| 217 | Walla Walla CO | 13
| 218 | Wapato | 10
| 219 | Washougal 8 ENE | 21
| 220 | Waterville | 1
| 221 | Wawawai 2 NW | 14
| 222 | Wellpinit | 1
| 223 | Wenatchee AP | 13
| 224 | Wenatchee CO | 10
| 225 | West Clarkston | 10
| 226 | Whidbey Island | 11
| 227 | White River RS | 12
| 228 | White Swan RS | 8
| 229 | Whitman Mission | 11
| 230 | Wilbur | 4
| 231 | Willapa Harbor | 26
| 232 | Wilson Creek | 3
| 233 | Wind River | 15
| 234 | Winthrop 1 WSW | -12
| 235 | Yakima AP | 11